EXISTING CONDITIONS REPORT — Interior Office Fitout WHA Office Suite 220 Wilmington Housing Authority · 2nd Floor Office Suite Project No. [M4D-2026-___] — Date: April 2026 — Prepared by: Merge 4 Design LLC

01 — PROJECT INFORMATION

| Project | WHA Office Suite 220 — Interior Office Fitout |
| --- | --- |
| Address | [Building Address], Wilmington, Delaware |
| Client / Owner | Wilmington Housing Authority (WHA) |
| Project Lead | Merge 4 Design LLC (M4D) |
| AOR | David C. Ainsworth AIA · Aubyn Architecture LLC · DE Lic. #[NO] |
| Report Date | April 2026 |
| Report Type | Existing Conditions — Photo Survey with Dimensional Analysis |
| Suite Numbers | 220, 220A, 220B, 220C, 220D, 220E, 221 |
| Floor | 2nd Floor |

| NOTE | Dimensional data in this report is based on one confirmed field measurement (main room 19'×24'), one confirmed ceiling height (9'-0" AFF to underside of ACT grid), one confirmed door width (42"), and one confirmed window sill height (36.5" AFF). All other dimensions are estimated proportionally from photographic analysis. All estimated dimensions must be field-verified prior to construction document production. |
| --- | --- |

02 — SURVEY METHODOLOGY

This report was prepared using a photographic survey of the existing suite. Video captures and still photography were collected on site. Key dimensions were field-measured at time of capture. All remaining dimensions were estimated using proportional analysis against confirmed reference dimensions, with the 2'×4' ACT ceiling grid module used as a secondary dimensional reference throughout.

Wall construction confirmed as CMU (concrete masonry unit) throughout, except Room 220D which has GWB (gypsum wallboard) partition walls. CMU block course height (nominal 8") visible in photos was used as an additional dimensional calibration reference.

03 — ROOM SCHEDULE

| Room | Description | Length | Width | Area (est.) | Notes |
| --- | --- | --- | --- | --- | --- |
| 220 | Main open room | 24'-0" | 19'-0" | 456 SF | Confirmed field dims. Yellow/green/blue walls. |
| 220A | Blue secondary office | 20'-0" est. | 15'-0" est. | 300 SF est. | Window wall, 2 windows. CMU. |
| 220B | Work room | 15'-0" est. | 12'-0" est. | 180 SF est. | Sink confirmed. Interior window. CMU. |
| 220C | L-shaped anteroom | 18'-0" est. | 14'-0" est. | 220 SF est. | Partial-height drywall partition (~6'). HVAC diffuser confirmed. |
| 220D | Small office | 12'-0" est. | 10'-0" est. | 120 SF est. | GWB walls (not CMU). Raceway strip. VCT removed. |
| 220E | Small office | 12'-0" est. | 10'-0" est. | 120 SF est. | Adjacent to 220D. Not fully photographed. |
| 221 | Entry vestibule | 10'-0" est. | 7'-6" est. | 75 SF est. | Suite entry from main corridor. Narrow. 2'×2' fixture. |
| TOTAL | Suite 220 — All rooms | ~1,471 SF | Estimated — verify by field measure |

04 — DOOR SCHEDULE

| Door | Location | Width | Height | Type | Hardware | Notes |
| --- | --- | --- | --- | --- | --- | --- |
| D-01 | Room 220, blue wall | 3'-6" (42") | 7'-0" est. | Wood veneer, HCF | Lever, standard | Confirmed width. Opens to corridor. |
| D-02 | Room 220A entry | 3'-0" est. | 7'-0" est. | Wood veneer, HCF | Lever, standard | Interior connecting door. |
| D-03 | 220C suite entry | 3'-0" est. | 7'-0" est. | Wood veneer, HCF | Lever, standard | Suite entry from corridor. |
| D-04 | Room 220B rear | 3'-0" est. | 7'-0" est. | Wood veneer, HCF | Lever, standard | Connects to secondary space. |
| D-05 | 220D (Room 221 entry) | 3'-0" est. | 7'-0" est. | Wood veneer, HCF | Lever, 3-hinge | Label: 220D. Opens into room. |
| D-06 | 220E entry | 3'-0" est. | 7'-0" est. | Wood veneer, HCF | Lever, standard | Label: 220E. Adjacent to 220D. |

HCF = Hollow Core Flush. All door frames: dark stained wood, brown. All existing hardware: lever set. Verify fire rating status of all doors — door 220C (suite entry) has closer installed suggesting possible rated assembly.

05 — WINDOW SCHEDULE

| Win. | Location | Sill HT | Head HT | Width Est. | Type | Notes |
| --- | --- | --- | --- | --- | --- | --- |
| W-01 | Room 220, main wall | 2'-10½" (36.5") | 7'-4" est. | ~20'-0" | Fixed ribbon | Confirmed sill. Near full wall width. Mullions. |
| W-02 | Room 220, side wall | 2'-10½" | 7'-4" est. | ~4'-0" | Fixed | Single unit. Vertical blinds. |
| W-03 | Room 220A, window wall | 2'-10½" | 7'-4" est. | ~8'-0" | Fixed, 2 units | Two units with mullion. Vertical blinds. |
| W-04 | Room 220C, exterior | 2'-10½" | 7'-4" est. | ~4'-0" | Fixed | Single unit. Vertical blinds. |
| W-05 | Room 220D / 220E | 2'-10½" | 7'-4" est. | ~4'-0" | Fixed | One unit confirmed. Verify 220E. |
| IW-01 | 220B / 220C interior | N/A | N/A | ~3'×3' | Wire/frosted glass | Borrowed light. CMU opening. Verify glazing type. |

All exterior windows: vertical blinds, wood-grain surround trim. Blue accent paint band above window head approximately 18" tall at Room 220. Sill height 36.5" AFF is a confirmed field measurement and is consistent across all spaces.

06 — CEILING, LIGHTING & MEP SCHEDULE

06.A  Ceiling System

| Element | Condition | Notes |
| --- | --- | --- |
| ACT grid system | Fair | 2'×4' suspended steel T-bar. Full suite. Grid intact — tiles missing throughout. Paint existing grid gray to match Suite 232 finish reference. |
| Grid height | Confirmed | 9'-0" AFF, underside of grid. Confirmed field measurement. Consistent all spaces. |
| ACT tiles | Missing | Majority missing throughout suite. Replace with new 2'×4' white fissured tile to match suite 232. |
| Open plenum | Exposed | Structural slab above. EMT conduit, flex duct, data conduit all visible. Coordinate all new MEP in plenum before tile installation. |

06.B  Lighting

| ID | Location | Type | Qty | Notes |
| --- | --- | --- | --- | --- |
| LF-01 | Room 220 | 2'×4' troffer | 2 confirmed | Fluorescent. Replace with LED throughout. Additional fixtures likely — verify when tiles removed. |
| LF-02 | Room 220A | 2'×4' troffer | 2 confirmed | Fluorescent. Replace with LED. |
| LF-03 | Room 220B | 2'×4' troffer | 1 confirmed | Fluorescent. Replace with LED. |
| LF-04 | Room 220C | 2'×4' troffer | 3 confirmed | Best lit space. Fluorescent. Replace with LED. |
| LF-05 | Room 221 | 2'×2' troffer | 1 confirmed | 2'×2' unit — note different size from other spaces. Narrow vestibule grid. |
| LF-06 | Rooms 220D/220E | TBD | TBD | Not clearly visible in photos. Verify in field. |

06.C  Fire Protection

| ID | Location | Type | Status | Notes |
| --- | --- | --- | --- | --- |
| SP-01 | Room 220 | Pendant sprinkler head | Active | Confirmed. ~3' from green wall, ~6' from blue wall. Estimated location. |
| SP-02 | Room 220 | Pendant sprinkler head | Active | Second head confirmed. Verify all head locations with fire suppression contractor. |
| SP-03 | Room 220A | Pendant sprinkler head | Active | One head confirmed. |
| SD-01 | Room 220 | Smoke detector | Active | Surface mount to grid tee. |
| SD-02 | Room 220B | Smoke detector | Active | Surface mount. Visible in photo. |

06.D  HVAC

| ID | Location | Type | Notes |
| --- | --- | --- | --- |
| HV-01 | Room 220C ceiling | 2'×2' supply diffuser | Only confirmed ceiling diffuser in suite. Location: right side ceiling. Verify supply/return status. |
| HV-02 | Room 220 plenum | Flex duct ~10" dia. | Visible in plenum, not connected to diffuser. Trace routing — determine if active or abandoned. |
| HV-03 | All spaces | TBD | No additional supply or return diffusers confirmed in photos. Verify existing HVAC system with building engineer before design. Perimeter baseboard or corridor supply possible. |

07 — ELECTRICAL SCHEDULE

| ID | Location | Type | Height AFF | Notes |
| --- | --- | --- | --- | --- |
| EL-01 | Room 220, green wall | Duplex outlet | ~18" | Standard height. Location estimated from photo. |
| EL-02 | Room 220D, back wall | Surface raceway, multi-outlet | ~36" | Continuous raceway ~6'-0" long. Desk-height power strip. Retain or remove per design. |
| EL-03 | Room 220D, left wall | Duplex outlet | Standard | Near window. Standard height. |
| SW-01 | Room 221, left wall | Switch plate | ~48" | Visible in corridor/vestibule photo. |
| SW-02 | Room 220C, left wall | Switch plate | ~48" | Visible in photo 5, batch 2. |

| NOTE | Existing electrical panel location not confirmed in photos. Locate and document panel before design. Verify circuit capacity for new LED fixture load and any new partition outlet requirements. |
| --- | --- |

08 — PLUMBING SCHEDULE

| ID | Location | Type | Notes |
| --- | --- | --- | --- |
| PL-01 | Room 220B / 220C junction | Wall-hung lavatory | White porcelain. Single faucet. Stub-outs visible at CMU wall. Confirm hot/cold supply and drain are active (not capped). Retain or relocate per design. |

No additional plumbing fixtures confirmed. Verify if floor drain exists in any space — not visible in photos. Coordinate sink location with new partition layout prior to MEP rough-in.

09 — EXISTING FINISHES

| Element | Existing Condition | Action / Notes |
| --- | --- | --- |
| Floor — Rooms 220, 220A, 220B, 220C | VCT, cream/tan, 12''×12'' tile | Remove. Replace with LVP to match finish reference. |
| Floor — Room 220D | VCT removed, bare concrete/adhesive | Prep slab. Install LVP to match finish reference. |
| Floor — Room 220E | TBD — not confirmed | Verify in field. Assume VCT removal required. |
| Walls — CMU spaces | Painted CMU, multiple colors | New work: GWB on metal stud. Paint all surfaces to match finish reference — light warm gray. |
| Walls — Room 220D | GWB, painted. Cracking visible. | Repair cracks, skim, repaint to match finish reference. |
| Ceiling — ACT tiles | Majority missing throughout | Replace all missing tiles with 2'×4' white fissured ACT. Full suite. |
| Ceiling — ACT grid | Existing steel T-bar, white | Paint existing grid gray to match Suite 232. Do not replace grid unless damaged. |
| Base | Existing base not clearly confirmed | Install new 4'' cove base — black or dark charcoal rubber/vinyl to match Suite 232. |
| Doors — existing | Wood veneer, dark brown frame | Refinish or replace per budget. New doors: painted gray to match Suite 232. |
| Hardware — existing | Lever set, dark finish | Replace with brushed stainless or satin chrome lever to match Suite 232. |
| Light fixtures | Fluorescent 2'×4' troffers throughout | Replace all with 2'×4' LED troffers to match Suite 232. Verify switching. |

10 — FINISH REFERENCE — SUITE 232 (ADJACENT SUITE)

The following finishes are confirmed from photographic documentation of Suite 232 — the adjacent finished suite across the main corridor. All new work in Suite 220 shall match Suite 232 finishes. Coordinate with WHA facilities and building management to confirm product specifications and sourcing.

| Finish Element | Description | Specification Notes |
| --- | --- | --- |
| Floor | LVP plank — gray/weathered wood | ~6'' wide planks. Gray tone with subtle wood grain. Running perpendicular to window wall. Obtain product spec from WHA — match existing Suite 232 installation. |
| Wall paint | Light warm gray — GWB smooth | Applied to new GWB partitions and existing CMU (skim coat or fur out). Match Suite 232 color exactly — obtain paint chip from building management. |
| Ceiling tile | 2'×4' white fissured ACT | Standard commercial fissured pattern. White. 15/16'' grid. Armstrong or equivalent. Replace all missing tiles full suite. |
| Ceiling grid | Painted gray — match wall color | Paint existing T-bar grid. Do not replace unless damaged. Match Suite 232 grid color. |
| Base | 4'' cove base — black / dark charcoal | Rubber or vinyl cove base. Black or very dark charcoal. Continuous around all walls. |
| Door leaf (new) | Painted gray flush door | Match Suite 232 gray painted doors. Hollow metal or solid core painted wood. |
| Door frame (new) | Painted gray, knocked-down frame | Match Suite 232 gray painted frames. |
| Hardware | Lever set — brushed stainless / satin chrome | Match Suite 232. Schlage or equivalent commercial grade. |
| Light fixtures | 2'×4' LED troffer — white lens | Replace existing fluorescent throughout. Match Suite 232 fixture type. Verify lumen output and color temperature. |

11 — FIELD VERIFICATION CHECKLIST

The following items must be field-verified prior to construction document production. This list is not exhaustive — any dimension marked "est." in this report requires physical verification.

| # | Item to Verify | Priority |
| --- | --- | --- |
| 1 | Overall suite perimeter dimensions — verify all room widths and lengths with tape or laser measure | HIGH |
| 2 | CMU wall thickness — confirm nominal 8" throughout | HIGH |
| 3 | Window opening widths and heights — all windows | HIGH |
| 4 | Room 220E — document fully (not photographed) | HIGH |
| 5 | Locate electrical panel — confirm location and capacity | HIGH |
| 6 | Confirm plumbing rough-in at sink is active (not capped) | HIGH |
| 7 | Trace HVAC flex duct in Room 220 plenum — confirm routing and termination | MEDIUM |
| 8 | Confirm all sprinkler head locations — coordinate with fire suppression contractor | MEDIUM |
| 9 | Verify ACT grid condition — identify any damaged sections requiring replacement | MEDIUM |
| 10 | Confirm fire rating status of suite entry door (220C) — door closer noted | MEDIUM |
| 11 | Document Room 220D drywall crack condition — determine if structural or cosmetic | MEDIUM |
| 12 | Obtain Suite 232 finish specifications from WHA facilities — floor, paint, tile product data | MEDIUM |
| 13 | Confirm interior window (IW-01) glazing type — wire glass or other | LOW |
| 14 | Confirm corridor finish floor type and thickness — affects new flooring transition detail | LOW |

12 — REVIT MODELING SEQUENCE

Build the existing conditions Revit model in the following sequence. Use confirmed dimensions as anchor points and estimated dimensions as placeholders pending field verification.

| Step | Element | Method | Dims |
| --- | --- | --- | --- |
| 1 | Suite perimeter — CMU walls | Draw from Room 220 confirmed 19'×24'. Extend north/south to establish full perimeter. Use 8'' CMU wall type. | Confirmed |
| 2 | Interior CMU walls — room divisions | Add interior walls based on door locations and proportional estimates. Place as schematic — adjust after field verification. | Estimated |
| 3 | All doors — D-01 through D-06 | Place at estimated locations. D-01 confirmed 42''. All others 36'' nom. pending verification. | Partial |
| 4 | All windows — W-01 through W-05 | Exterior windows at sill 36.5'' AFF confirmed. Head height 7'-4'' estimated. Widths estimated. | Partial |
| 5 | Interior window — IW-01 | CMU opening. Place as 3'×3' window family. Verify glazing type in field. | Estimated |
| 6 | Partial-height partition — Room 220C | Blue element. GWB partition family, height 6'-0'' est. Does not extend to ceiling. | Estimated |
| 7 | Ceiling — ACT grid at 9'-0'' AFF | Revit ceiling: 2'×4' ACT grid, height 9'-0''. Apply to all rooms. Confirmed dimension. | Confirmed |
| 8 | Light fixtures | Place 2'×4' troffer families at grid locations per schedule. 2'×2' in Room 221. | Estimated |
| 9 | Sprinkler heads | Place pendant head families at estimated photo locations. Confirm with fire sub. | Estimated |
| 10 | Plumbing — sink | Wall-hung lav family at 220B/220C junction. Verify rough-in location in field. | Estimated |
| 11 | Electrical devices | Place duplex outlets and switches at schedule locations. Raceway strip in 220D. | Estimated |
| 12 | Apply materials / finishes | Apply existing finish materials for EC documentation. Update to new finishes in design model. | Reference |

Merge 4 Design LLC  —  WHA Suite 220 Existing Conditions Report  —  April 2026

PRELIMINARY — NOT FOR CONSTRUCTION  |  All dimensions require field verification prior to CD production